SURFACE MOUNTED PRESSURE-RELIEF LOUVRE TYPE RENSON 433L

SPECIFICATION SHEET

Louvre type Renson 433L is a surface mounted pressure-relief louvre and has the following properties:

- Aesthetics

  - Blade pitch = 99 mm

  - Invisible fixings

  - mitred, pressed corners

- airflow

  - Closed up to +/- 8 Pa pressure drop over the louvre

  - Dependent of dimensions and pressure drop:

| Dimensions (wxh) | Airflow at 10Pa pressure drop | Airflow at 50Pa pressure drop |
| --- | --- | --- |
| 328mm x328mm | 126 m³/h | 1311 m³/h |
| 428mm x428mm | 246 m³/h | 2565 m³/h |
| 528mm x528mm | 405 m³/h | 4220 m³/h |

- Material

  - extruded aluminium profiles (AlMgSi0.5, EN AW 6063 T66)

  - surface treatment:

    - anodised in natural colour EV6/EV1 (20 micron): pretreated and anodised OR

    - polyester powder coating in RAL colour according to the Qualicoat standard

- louvre depth : 29mm