Invisivent® AIR Light

Renson Ventilation, IZ 2 Vijverdam, Maalbeekstraat 10, 8790 Waregem – Belgium

Tel. +32 (0)56 62 71 11, fax +32 (0)56 60 28 51, info@renson.be www.renson.eu

product features (text marked in red can be deleted at your discretion)

- Type: Thermally broken, noise-reducing, self-regulating valve ventilation for installation on the window

- Acoustic comfort:

  - Equipped as standard with acoustic damping material 
(PEPP – Porous Expanded Polypropylene)

  - Integrated acoustic material: no additional acoustic module to the inside

- Self-regulating valve (P3):

  - Self-regulating effect at pressure differences as of 2 Pa

  - Automatically responds to pressure differences/wind strength and cannot be influenced by the user

  - Ensures constant airflow and reduces energy losses

- Adjustable aluminium inner valve directs the airflow upwards: Coandă effect

- Non-punched, controllable inner valve with gripping edge: 5 positions

- Condensation-free, due to the thermally insulating profile on the inner valve

- Insect-proof: invisible, perforated inner profile (3.9 x 9.8 mm)

- Easy cleaning: Removable inner profile

- Controls: manual, cord, rod, motor

- Finish:

  - Anodised (F1) / powder-coated in the same RAL colour as the window profiles / bicolour

  - Colour of endcaps = standard mass end caps (best match), mass end caps of your choice, coated endcaps

- Construction height: 65 mm / visible outside opening: 33 mm

- Recessed installation on the window profile (0 mm glass reduction):

  - Suitable for window profile thicknesses of 50 to 202 mm (and thicker on request)

  - Completely recessed installation both indoors and outdoors (completely invisible)

  - Optional designer outer cover available

- Perfect airtight connection to the window profile due to coextruded, flexible sealing over the entire length of the window ventilation, including the endcaps.

- Installation:

  - Directly anchor the window ventilation to the window with screws

    - Screw zone provided in the PVC body

    - Additional screw zone through the aluminium outer profile makes it possible to anchor the product at any time without damaging the thermal bridge of the window profile

    - Quick and easy installation due to the monobloc principle

  - Guaranteed stability of window and louvre due to monobloc principle + additional reinforcement with screws in body (every 280 mm)

  - Integrated Euronut dowel slot for good anchoring to the wall

- Flexible and aesthetic interior finishing:

  - Airtight wet plastering: easy to do due to removable vertical rib, which allows a standard plaster profile (commercially available) to be used.

  - By removing the vertical rib, a recess is created in which an MDF board, plasterboard, or PVC panel can be placed.

  - A buffer area prevents plastering of the inner valve

- Optionally available with Pollux filter: for rooms with high particulate and pollen levels

APPLICATION

- Can be combined with Invisivent COMFORT in the same project due to the identical look & feel

- Dimensioned at 2 Pa: can be used in every project as standard

performance level

- U value: 				2.0 W/(m²K)

- F value:				0.78

- Water resistance up to: 		900 Pa in closed position

- Water resistance up to: 		150 Pa in open position

250 Pa in open position (with design exterior cover)

- Leakage rate at 50 Pa:		< 15% (in closed position)

- Burglar resistance:		class 2 (if window is WK2)

- Sound damping Dn,e,w (C;Ctr):

- In open position:	31(-1;-2) dB

- In closed position: 	51 (-1;-3) dB

| Properties: |  |
| --- | --- |
| Airflow Q at 1 Pa | 10.6 l/s/m |
| Airflow Q at 1 Pa | 38.1 m³/h/m |
| Airflow Q at 2 Pa | 17.2 l/s/m |
| Airflow Q at 2 Pa | 62.0 m³/h/m |
| Airflow Q at 10 Pa | 16.4 l/s/m |
| Airflow Q at 20 Pa | 19.2 l/s/m |
| Equivalent area | 13479 mm²/m |
| Self-regulating | yes |
| Surface area | 0.065 m²/m |