RENSON LINIUS® L.033.01

SPECIFICATION SHEET

LINIUS® L.033.01 is a ventilation system composed of continuous louvres with the following essential characteristics:

- aesthetically appealing

  - visual protection

    - horizontally visually closed by applying a blade pitch which does not exceed the blade height

    - blade pitch: 33.33 mm

    - blade height: 37 mm

  - invisible assembly with aluminium blade clips

- airflow

  - physical free area: 50%

  - visual free area: 60%

  - aerodynamic properties according to EN 13030:2001 (with mesh 2.3 x 2.3 mm)

    - resistance factor entry K = 1/ce² = 20.47  /  Ce = 0.221

    - class 3

  - documents to be submitted : independent test report in accordance with EN 13030:2001 to determine the aerodynamic properties (BSRIA, 101477/1)

- Weatherability (EN 13030:2001)

  - with mesh 2.3 x 2.3 mm and threshold profile

    - class A at 0.5 m/s air entry

    - class B at 1.0 m/s air entry

  - documents to be submitted : independent test report in accordance with EN 13030:2001 to determine the aerodynamic properties (BSRIA, 101477/1)

- stability

  - impact of wind forces :

    - Cfx :  -1,61 (drag - horizontal)

    - Cfy :  0,73 (lift - vertical)

    - documents to be submitted : independent report of wind tunnel measurenments of the aerodynamic forces on louvres. (VUB - 2018)

  - strength of blade connection:

    - documents to be submitted : independent test report to determine the strength of the blade connection (TÜV)

  - max. unsupported blade span at a peak velocity pressure qp(z) of 800 Pa: 800 mm

  - supporting structure

    - type of mullion and number of mullions are to be provided according to the designed span and the local wind load

    - preferably in aluminium, as part of the continuous louvre system

- materials:

  - extruded aluminium profiles (AlMgSi0.5, EN AW 6063 T66)

  - surface treatment:

    - anodised in natural colour EV6/EV1 (20 micron): pretreated and anodised OR

    - polyester powder coating in RAL colour according to the Qualicoat standard

- options

  - wire mesh 2.3 x 2.3 ; 6 x 6 of 20 x 20 mm, fitted to the rear of the supporting structure

  - threshold profile LZ.4140

  - pre-assembled pivoting ventilation doors with linear blades (see separate description)