RENSON LOUVRE SPECIFICATIONS 
Brand
: LOUVRE PANEL 
Type 

: 475 – BUILT-IN 75 mm pitch wall louvre
Manufacture and reference :

The 475 Louvre Panel is manufactured and supplied by Renson Ventilation Tel: 0032 56 62 71 11
Email: info@renson.be Website: www.renson.de
Description:
RENSON 475 is an aluminium louvre panel consisting of extruded weatherable blades L.075W mounted into an integrated frame. It is designed to be built into a pre formed opening. It is supplied with a flanged frame, stainless steel mesh 2,3 x 2,3 mm and a water channel at the bottom.
The louvre 475 applies to class A2 at a wind velocity of 13 m/s and a suction fan speed of 0 m/s, according to EN13030:2001. BSRIA certificate available. Ideal for using in discharge applications where water protection is required.
System operation and Airflow Performance (with SS insect mesh 2,3mm x 2,3mm secured to the rear)
Airflow:




· K-factor: Intake


10.89
· K-factor: Discharge

10.41
· Ce coefficient: Intake

0.303
· Cd coefficient: Discharge
0.310
Free area:

· Physical Free Area

53%

· Visual Free Area

87%

Water protection:
The louvre 475 applies to effectiveness class A2 at a suction fan speed of 0 m/s.

· Effectiveness class @ 0,0 m/s: 
A2
· Effectiveness class @ 0,5 m/s: 
B2
· Effectiveness class @ 1,0 m/s: 
B2
· Effectiveness class @ 1,5 m/s: 
C2
· Effectiveness class @ 2,0 m/s: 
D2

Dimensions/Size Range:

Minimum Dimensions (mm)
200 x 295
Flange Height (mm)
50
Pitch (mm)
75
Built-in depth (mm)
82 

Total depth (mm)
87 

Remark: In order to strengthen the whole construction, louvres wider than 700 mm are provided with an extra perforated U-profile to fix additional blade supports.

Product Construction:
Profile: Extruded aluminium (EN 12020-2)

Surface Treatment:

Mill finish

Anodised (EV6/EV1) (20 micron): pre-treated and anodised.

Polyester powder coating in any RAL colour (60-80 micron): aluminium profiles pre-treated to resist corrosion to guarantee.

Installation: 

To be built into a reveal. Bracket 429 included. Reinforcing structure needed on panels larger than 3m2
