BUILT-IN WALL LOUVRE TYPE RENSON 411

SPECIFICATION SHEET

Louvre type Renson 411 is a built-in ventilation louvre and has the following properties :

- aesthetics

  - visual screening

    - horizontally visually closed, by applying a blade pitch which does not exceed the blade height

    - blade pitch = 33.33 mm

    - blade height = 37 mm

  - invisibly assembled with aluminium blade supports

  - Invisible mounting of the louvre with wall anchors no. 418.

  - mitred, pressed corners

  - flange = 21mm

- airflow

  - physical free area: 50%

  - visual free area: 60%

  - aerodynamic properties according to EN 13030:2001 (with mesh 2.3 x 2.3 mm)

    - resistance factor entry K = 1/ce² = 20.47  /  ce = 0.221

    - class 3

  - documents to be submitted : independent test report in accordance with EN 13030:2001 to determine the aerodynamic properties (BSRIA, 101477/1)

- Weatherability (EN 13030:2001)

  - with mesh 2.3 x 2.3 mm and water channel

    - class A at 0.5 m/s air entry

    - class B at 1.0 m/s air entry

  - documents to be submitted : independent test report in accordance with EN 13030:2001 to determine the aerodynamic properties (BSRIA, 101477/1)

- stability

  - For louvres larger than 3 m², a reinforcing mullion to be provided.

- material

  - extruded aluminium profiles (AlMgSi0.5, EN AW 6063 T66)

  - made with mesh composed of stainless steel 18/8: mesh size 2.3 x 2.3 mm

  - surface treatment:

    - anodised in natural colour EV6/EV1 (20 micron): pretreated and anodised OR

    - polyester powder coating in RAL colour according to the Qualicoat standard

- fitting depth : 29mm

- options

  - Alternative mesh types: mesh size 6mm x 6mm or 10mm x 10mm.

  - Water channel for increased weatherability: class A3 at 0,5 m/s (BSRIA, 101477/1)

  - Drainage profile to prevent dirt deposits on the facade

  - Removable mesh: allows easy cleaning and comes with an integrated drainage profile

  - Filter: class G4

  - Without flange