LINIUS® SPECIFICATIONS

Brand	: RENSON LINIUS®

Type 		: L.050W with holder LD.0065 (VV-L-1.3701)

Description:

RENSON LINIUS® lourve system L.050W is compiled from sections of extruded aluminium ALMgSi0.5 that have undergone a surface treatment in accordance with the architect’s specifications. The system consists of water-resistant ventilation strips (tested in accordance with Hevac) – with a large physical free area and an ideal K-factor. It is easily and invisibly mounted due to the assembly clips that fit into the strip holders that form part of the system.

Standards:

- Aluminium alloy: Al Mg Si 0.5 (F25)

- Standardisation: EN AW-6063

- Hardening: T66

- Aluminium pre-treatment:

- Standard DIN 50021 SS

- Strength calculations are based on the following standards:

- ENV 1999-1-1: Calculation of structures in aluminium

- NBN B-03-002-2: Wind load – Dynamic effects

- EN 1991-1-4: Wind load

Surface treatment:

- Natural anodised colour F1 (20 micron): Pre-treated and anodised

- Polyester powder coating in RAL colours (60 to 80 micron): aluminium profiles pre-treated to resist corrosion (DIN 5002155) to guarantee a strong powder layer, and subsequently thermally lacquered

System operation:

- Strips:

- Water-resistant strips with a large clearance, L.050W from extruded aluminium

- Water-resistance classification in accordance with HEVAC (officially tested): A2 through 3 m/s

- Dimensions:

    - Height:  89.6 mm

    - Depth: 130.0 mm

    - Step: 50.0 mm (20 strips across a 1 metre height)

    - Average strip gradient: 44°

- Minimum moments of inertia Iy = 778,472 mm4 (strong axis line) ;  Iz = 100,395 mm4, with a minimum material thickness of 1.8 mm

- Drag coefficient:

    - Cfy (determined by means of wind tunnel testing):  1.3 (horizontal direction)

    - Cfz (determined by means of wind tunnel testing):  0.95 (vertical direction)

- Invisibly mounted using clips that fit into the accompanying strip holder L.050W.11 and L.050W.12 (clip joints)

- Physical allowed clearance: 57%

- K-factor: 10.47

- Strip is fitted with 2 screw ducts, suitable for screws of DIN 7982 – ST3.9 mm type

- Inox / stainless steel mesh grid 2.3 x 2.3 mm secured at the back

- Support structure:

- Support profile LD.0065 from extruded aluminium: 30 x 6.5 mm

- Minimum moment of inertia Iy = 261 mm4

- Strip holders are pre-mounted to the holder profile LD.0065

- Mounting the support profile directly onto the rear support structure

- Means of attachment consists of corrosion resistant material

- Overstretch:

- Maximum possible allowed overstretching of the described system, with a wind load qb = 800 Pa:

    - Strip L.050W:  1,900 mm

    - Support profile LD.0065: Mounting directly onto the rear support structure

- System depth:

- Strip L.050W and support profile LD.0065: 139 mm

LINIUS® SPECIFICATIONS

Brand	: RENSON LINIUS®

Type 		: L.050W with holder LD.0195 (VV-L-1.3702)

Description:

RENSON LINIUS® lourve system L.050W is compiled from sections of extruded aluminium ALMgSi0.5 that have undergone a surface treatment in accordance with the architect’s specifications. The system consists of water-resistant ventilation strips (tested in accordance with Hevac) – with a large physical free area and an ideal K-factor. It is easily and invisibly mounted due to the assembly clips that fit into the strip holders that form part of the system.

Standards:

- Aluminium alloy: Al Mg Si 0.5 (F25)

- Standardisation: EN AW-6063

- Hardening: T66

- Aluminium pre-treatment:

- Standard DIN 50021 SS

- Strength calculations are based on the following standards:

- ENV 1999-1-1: Calculation of structures in aluminium

- NBN B-03-002-2: Wind load – Dynamic effects

- EN 1991-1-4: Wind load

Surface treatment:

- Natural anodised colour F1 (20 micron): Pre-treated and anodised

- Polyester powder coating in RAL colours (60 to 80 micron): aluminium profiles pre-treated to resist corrosion (DIN 5002155) to guarantee a strong powder layer, and subsequently thermally lacquered

System operation:

- Strips:

- Water-resistant strips with a large clearance, L.050W from extruded aluminium

- Water-resistance classification in accordance with HEVAC (officially tested): A2 through 3 m/s

- Dimensions:

    - Height:  89.6 mm

    - Depth: 130.0 mm

    - Step: 50.0 mm (20 strips across a 1 metre height)

    - Average strip gradient: 44°

- Minimum moments of inertia Iy = 778,472 mm4 (strong axis line); Iz = 100,395 mm4, with a minimum material thickness of 1.8 mm

- Drag coefficient:

    - Cfy (determined by means of wind tunnel testing):  1.3 (horizontal direction)

    - Cfz (determined by means of wind tunnel testing):  0.95 (vertical direction)

- Invisibly mounted using clips that fit into the accompanying strip holder L.050W.11 and L.050W.12 (clip joints)

- Physical allowed clearance: 57%

- K-factor: 10.47

- Strip is fitted with 2 screw ducts, suitable for screws of DIN 7982 – ST3.9 mm type

- Inox / stainless steel mesh grid 2.3 x 2.3 mm secured at the back

- Support structure:

- Support profile LD.0195 from extruded aluminium: 36 x 17.5 mm

- Minimum moments of inertia Iz = 5,931 mm4

- Strip holders are pre-mounted to the holder profile LD.0195

- Mounting of the support profiles occurs using attachment elements LZ.4211 and LZ.4209 or guiding attachment element LZ.4206

- Attachment elements consist of corrosion resistant material

- Overstretch:

- Maximum possible allowed overstretching of the described system, with a wind load qb = 800 Pa:

    - Strip L.050W:  1,900 mm

    - Support profile LD.0195: 533 mm

- System depth:

- Strip L.050W and support profile LD.0195: 150 mm

LINIUS® SPECIFICATIONS

Brand	: RENSON LINIUS®

Type 		: L.050W with holder LD.0460 (VV-L-1.3703)

Description:

RENSON LINIUS® lourve system L.050W is compiled from sections of extruded aluminium ALMgSi0.5 that have undergone a surface treatment in accordance with the architect’s specifications. The system consists of water-resistant ventilation strips (tested in accordance with Hevac) – with a large physical free area and an ideal K-factor. It is easily and invisibly mounted due to the assembly clips that fit into the strip holders that form part of the system.

Standards:

- Aluminium alloy: Al Mg Si 0.5 (F25)

- Standardisation: EN AW-6063

- Hardening: T66

- Aluminium pre-treatment:

- Standard DIN 50021 SS

- Strength calculations are based on the following standards:

- ENV 1999-1-1: Calculation of structures in aluminium

- NBN B-03-002-2: Wind load – Dynamic effects

- EN 1991-1-4: Wind load

Surface treatment:

- Natural anodised colour F1 (20 micron): Pre-treated and anodised

- Polyester powder coating in RAL colours (60 to 80 micron): aluminium profiles pre-treated to resist corrosion (DIN 5002155) to guarantee a strong powder layer, and subsequently thermally lacquered

System operation:

- Strips:

- Water-resistant strips with a large clearance, L.050W from extruded aluminium

- Water-resistance classification in accordance with HEVAC (officially tested): A2 through 3 m/s

- Dimensions:

    - Height:  89.6 mm

    - Depth: 130.0 mm

    - Step: 50.0 mm (20 strips across a 1 metre height)

    - Average strip gradient: 44°

- Minimum moments of inertia Iy = 778,472 mm4 (strong axis line); Iz = 100,395 mm4, with a minimum material thickness of 1.8 mm

- Drag coefficient:

    - Cfy (determined by means of wind tunnel testing):  1.3 (horizontal direction)

    - Cfz (determined by means of wind tunnel testing):  0.95 (vertical direction)

- Invisibly mounted using clips that fit into the accompanying strip holder L.050W.11 and L.050W.12 (clip joints)

- Physical allowed clearance: 57%

- K-factor: 10.47

- Strip is fitted with 2 screw ducts, suitable for screws of DIN 7982 – ST3.9 mm type

- Inox / stainless steel mesh grid 2.3 x 2.3 mm secured at the back

- Support structure:

- Support profile LD.0460 from extruded aluminium: 36 x 44.0 mm

- Minimum moments of inertia Iy = 83,348 mm4

- Strip holders are pre-mounted to the holder profile LD.0460

- Mounting of the support profiles occurs using attachment elements LZ.4211 and LZ.4209 or guiding attachment element LZ.4206

- Attachment elements consist of corrosion resistant material

- Overstretch:

- Maximum possible allowed overstretching of the described system, with a wind load qb = 800 Pa:

    - Strip L.050W:  1,900 mm

    - Support profile LD.0460: 1,321 mm

- System depth:

- Strip L.050W and support profile LD.0460: 177 mm

LINIUS® SPECIFICATIONS

Brand	: RENSON LINIUS®

Type 		: L.050W with holder LD.0995 (VV-L-1.3704)

Description:

RENSON LINIUS® lourve system L.050W is compiled from sections of extruded aluminium ALMgSi0.5 that have undergone a surface treatment in accordance with the architect’s specifications. The system consists of water-resistant ventilation strips (tested in accordance with Hevac) – with a large physical free area and an ideal K-factor. It is easily and invisibly mounted due to the assembly clips that fit into the strip holders that form part of the system.

Standards:

- Aluminium alloy: Al Mg Si 0.5 (F25)

- Standardisation: EN AW-6063

- Hardening: T66

- Aluminium pre-treatment:

- Standard DIN 50021 SS

- Strength calculations are based on the following standards:

- ENV 1999-1-1: Calculation of structures in aluminium

- NBN B-03-002-2: Wind load – Dynamic effects

- EN 1991-1-4: Wind load

Surface treatment:

- Natural anodised colour F1 (20 micron): Pre-treated and anodised

- Polyester powder coating in RAL colours (60 to 80 micron): aluminium profiles pre-treated to resist corrosion (DIN 5002155) to guarantee a strong powder layer, and subsequently thermally lacquered

System operation:

- Strips:

- Water-resistant strips with a large clearance, L.050W from extruded aluminium

- Water-resistance classification in accordance with HEVAC (officially tested): A2 through 3 m/s

    - Height:  89.6 mm

    - Depth: 130.0 mm

    - Step: 50.0 mm (20 strips across a 1 metre height)

    - Average strip gradient: 44°

- Minimum moments of inertia Iy = 778,472 mm4 (strong axis line); Iz = 100,395 mm4, with a minimum material thickness of 1.8 mm

- Drag coefficient:

    - Cfy (determined by means of wind tunnel testing):  1.3 (horizontal direction)

    - Cfz (determined by means of wind tunnel testing):  0.95 (vertical direction)

- Invisibly mounted using clips that fit into the accompanying strip holder L.050W.11 and L.050W.12 (clip joints)

- Physical allowed clearance: 57%

- K-factor: 10.47

- Strip is fitted with 2 screw ducts, suitable for screws of DIN 7982 – ST3.9 mm type

- Inox / stainless steel mesh grid 2.3 x 2.3 mm secured at the back

- Support structure:

- Support profile LD.0995 from extruded aluminium: 36 x 97.5 mm

- Minimum moments of inertia Iy = 625,740 mm4

- Strip holders are pre-mounted to the holder profile LD.0995

- Mounting of the support profiles occurs using attachment elements LZ.4211 and LZ.4209 or guiding attachment element LZ.4206

- Attachment elements consist of corrosion resistant material

- Overstretch:

- Maximum possible allowed overstretching of the described system, with a wind load qb = 800 Pa:

    - Strip L.050W:  1,900 mm

    - Support profile LD.0995: 2,452 mm

- System depth:

- Strip L.050W and support profile LD.0995: 230 mm

LINIUS® SPECIFICATIONS

Brand	: RENSON LINIUS®

Type 		: L.050W with holder SD.014 (VV-L-1.3705)

Description:

RENSON LINIUS® lourve system L.050W is compiled from sections of extruded aluminium ALMgSi0.5 that have undergone a surface treatment in accordance with the architect’s specifications. The system consists of water-resistant ventilation strips (tested in accordance with Hevac) – with a large physical free area and an ideal K-factor. It is easily and invisibly mounted due to the assembly clips that fit into the strip holders that form part of the system.

Standards:

- Aluminium alloy: Al Mg Si 0.5 (F25)

- Standardisation: EN AW-6063

- Hardening: T66

- Aluminium pre-treatment:

- Standard DIN 50021 SS

- Strength calculations are based on the following standards:

- ENV 1999-1-1: Calculation of structures in aluminium

- NBN B-03-002-2: Wind load – Dynamic effects

- EN 1991-1-4: Wind load

Surface treatment:

- Natural anodised colour F1 (20 micron): Pre-treated and anodised

- Polyester powder coating in RAL colours (60 to 80 micron): aluminium profiles pre-treated to resist corrosion (DIN 5002155) to guarantee a strong powder layer, and subsequently thermally lacquered

System operation:

- Strips:

- Water-resistant strips with a large clearance, L.050W from extruded aluminium

- Water-resistance classification in accordance with HEVAC (officially tested): A2 through 3 m/s

- Dimensions:

    - Height:  89.6 mm

    - Depth: 130.0 mm

    - Step: 50.0 mm (20 strips across a 1 metre height)

    - Average strip gradient: 44°

- Minimum moments of inertia Iy = 778,472 mm4 (strong axis line); Iz = 100,395 mm4, with a minimum material thickness of 1.8 mm

- Drag coefficient:

    - Cfy (determined by means of wind tunnel testing):  1.3 (horizontal direction)

    - Cfz (determined by means of wind tunnel testing):  0.95 (vertical direction)

- Invisibly mounted using clips that fit into the accompanying strip holder L.050W.11 and L.050W.12 (clip joints)

- Physical allowed clearance: 57%

- K-factor: 10.47

- Strip is fitted with 2 screw ducts, suitable for screws of DIN 7982 – ST3.9 mm type

- Inox / stainless steel mesh grid 2.3 x 2.3 mm secured at the back

- Support structure:

- Support profile SD.014 in combination with LD.108, from extruded aluminium: 40 x 14.5 mm

- Minimum moment of inertia Iy = 37,137.103 mm4

- Strip holders are pre-mounted to the holder profile SD.014

- Mounting the support profile directly onto the rear support structure

- Attachment elements consist of corrosion resistant material

- Overstretch:

- Maximum possible allowed overstretching of the described system, with a wind load qb = 800 Pa:

    - Strip L.050W:  1,900 mm

    - Support profile SD.014: Mounting directly onto the rear support structure

- System depth:

- Strip L.050W and support profile SD.014: 147 mm

LINIUS® SPECIFICATIONS

Brand	: RENSON LINIUS®

Type 		: L.050W with holder SD.054 (VV-L-1.3706)

Description:

RENSON LINIUS® lourve system L.050W is compiled from sections of extruded aluminium ALMgSi0.5 that have undergone a surface treatment in accordance with the architect’s specifications. The system consists of water-resistant ventilation strips (tested in accordance with Hevac) – with a large physical free area and an ideal K-factor. It is easily and invisibly mounted due to the assembly clips that fit into the strip holders that form part of the system.

Standards:

- Aluminium alloy: Al Mg Si 0.5 (F25)

- Standardisation: EN AW-6063

- Hardening: T66

- Aluminium pre-treatment:

- Standard DIN 50021 SS

- Strength calculations are based on the following standards:

- ENV 1999-1-1: Calculation of structures in aluminium

- NBN B-03-002-2: Wind load – Dynamic effects

- EN 1991-1-4: Wind load

Surface treatment:

- Natural anodised colour F1 (20 micron): Pre-treated and anodised

- Polyester powder coating in RAL colours (60 to 80 micron): aluminium profiles pre-treated to resist corrosion (DIN 5002155) to guarantee a strong powder layer, and subsequently thermally lacquered

System operation:

- Strips:

- Water-resistant strips with a large clearance, L.050W from extruded aluminium

- Water-resistance classification in accordance with HEVAC (officially tested): A2 through 3 m/s

- Dimensions:

    - Height:  89.6 mm

    - Depth: 130.0 mm

    - Step: 50.0 mm (20 strips across a 1 metre height)

    - Average strip gradient: 44°

- Minimum moments of inertia Iy = 778,472 mm4 (strong axis line); Iz = 100,395 mm4, with a minimum material thickness of 1.8 mm

- Drag coefficient:

    - Cfy (determined by means of wind tunnel testing):  1.3 (horizontal direction)

    - Cfz (determined by means of wind tunnel testing):  0.95 (vertical direction)

- Invisibly mounted using clips that fit into the accompanying strip holder L.050W.11 and L.050W.12 (clip joints)

- Physical allowed clearance: 57%

- K-factor: 10.47

- Strip is fitted with 2 screw ducts, suitable for screws of DIN 7982 – ST3.9 mm type

- Inox / stainless steel mesh grid 2.3 x 2.3 mm secured at the back

- Support structure:

- Support profile SD.054 in combination with LD.108, from extruded aluminium: 40 x 54.0 mm

- Minimum moment of inertia Iy = 208,672.103 mm4

- Strip holders are pre-mounted to the holder profile SD.054

- Attachment elements consist of corrosion resistant material

- Overstretch:

- Maximum possible allowed overstretching of the described system, with a wind load qb = 800 Pa:

    - Strip L.050W:  1,900 mm

    - Support profile SD.054: 1,795 mm

- System depth:

- Strip L.050W and support profile SD.054: 187 mm

LINIUS® SPECIFICATIONS

Brand	: RENSON LINIUS®

Type 		: L.050W with holder SD.100 (VV-L-1.3707)

Description:

RENSON LINIUS® lourve system L.050W is compiled from sections of extruded aluminium ALMgSi0.5 that have undergone a surface treatment in accordance with the architect’s specifications. The system consists of water-resistant ventilation strips (tested in accordance with Hevac) – with a large physical free area and an ideal K-factor. It is easily and invisibly mounted due to the assembly clips that fit into the strip holders that form part of the system.

Standards:

- Aluminium alloy: Al Mg Si 0.5 (F25)

- Standardisation: EN AW-6063

- Hardening: T66

- Aluminium pre-treatment:

- Standard DIN 50021 SS

- Strength calculations are based on the following standards:

- ENV 1999-1-1: Calculation of structures in aluminium

- NBN B-03-002-2: Wind load – Dynamic effects

- EN 1991-1-4: Wind load

Surface treatment:

- Natural anodised colour F1 (20 micron): Pre-treated and anodised

- Polyester powder coating in RAL colours (60 to 80 micron): aluminium profiles pre-treated to resist corrosion (DIN 5002155) to guarantee a strong powder layer, and subsequently thermally lacquered

System operation:

- Strips:

- Water-resistant strips with a large clearance, L.050W from extruded aluminium

- Water-resistance classification in accordance with HEVAC (officially tested): A2 through 3 m/s

- Dimensions:

    - Height:  89.6 mm

    - Depth: 130.0 mm

    - Step: 50.0 mm (20 strips across a 1 metre height)

    - Average strip gradient: 44°

- Minimum moments of inertia Iy = 778,472 mm4 (strong axis line); Iz = 100,395 mm4, with a minimum material thickness of 1.8 mm

- Drag coefficient:

    - Cfy (determined by means of wind testing):  1.3 (horizontal direction)

    - Cfz (determined by means of wind tunnel testing):  0.95 (vertical direction)

- Invisibly mounted using clips that fit into the accompanying strip holder L.050W.11 and L.050W.12 (clip joints)

- Physical allowed clearance: 57%

- K-factor: 10.47

- Strip is fitted with 2 screw ducts, suitable for screws of DIN 7982 – ST3.9 mm type

- Inox / stainless steel mesh grid 2.3 x 2.3 mm secured at the back

- Support structure:

- Support profile SD.100 in combination with LD.108, from extruded aluminium: 40 x 100.0 mm

- Minimum moment of inertia Iy = 1248,414.103 mm4

- Strip holders are pre-mounted to the holder profile SD.100

- Attachment elements consist of corrosion resistant material

- Overstretch:

- Maximum possible allowed overstretching of the described system, with a wind load qb = 800 Pa:

    - Strip L.050W:  1,900 mm

    - Support profile SD.100: 3,259 mm

- System depth:

- Strip L.050W and support profile SD.100: 233 mm

LINIUS® SPECIFICATIONS

Brand	: RENSON LINIUS®

Type 		: L.050W with holder LD.0440 (VV-L-1.3708)

Description:

RENSON LINIUS® lourve system L.050W is compiled from sections of extruded aluminium ALMgSi0.5 that have undergone a surface treatment in accordance with the architect’s specifications. The system consists of water-resistant ventilation strips (tested in accordance with Hevac) – with a large physical free area and an ideal K-factor. It is easily and invisibly mounted due to the assembly clips that fit into the strip holders that form part of the system.

Standards:

- Aluminium alloy: Al Mg Si 0.5 (F25)

- Standardisation: EN AW-6063

- Hardening: T66

- Aluminium pre-treatment:

- Standard DIN 50021 SS

- Strength calculations are based on the following standards:

- ENV 1999-1-1: Calculation of structures in aluminium

- NBN B-03-002-2: Wind load – Dynamic effects

- EN 1991-1-4: Wind load

Surface treatment:

- Natural anodised colour F1 (20 micron): Pre-treated and anodised

- Polyester powder coating in RAL colours (60 to 80 micron): aluminium profiles pre-treated to resist corrosion (DIN 5002155) to guarantee a strong powder layer, and subsequently thermally lacquered

System operation:

- Strips:

- Water-resistant strips with a large clearance, L.050W from extruded aluminium

- Water-resistance classification in accordance with HEVAC (officially tested): A2 through 3 m/s

- Dimensions:

    - Height:  89.6 mm

    - Depth: 130.0 mm

    - Step: 50.0 mm (20 strips across a 1 metre height)

    - Average strip gradient: 44°

- Minimum moments of inertia Iy = 778,472 mm4 (strong axis line); Iz = 100,395 mm4, with a minimum material thickness of 1.8 mm

- Drag coefficient:

    - Cfy (determined by means of wind testing):  1.3 (horizontal direction)

    - Cfz (determined by means of wind tunnel testing):  0.95 (vertical direction)

- Invisibly mounted using clips that fit into the accompanying strip holder L.050W.11 and L.050W.12 (clip joints)

- Physical allowed clearance: 57%

- K-factor: 10.47

- Strip is fitted with 2 screw ducts, suitable for screws of DIN 7982 – ST3.9 mm type

- Inox / stainless steel mesh grid 2.3 x 2.3 mm secured at the back

- Support structure:

- Support profile LD.0440 from extruded aluminium: 36 x 44.0 mm

- Minimum moments of inertia Iy = 83,228 mm4

- Strip holders are pre-mounted to the holder profile LD.0440

- Mounting of the support profiles occurs using attachment elements LZ.4211 and LZ.4209 or guiding attachment element LZ.4206

- Sideways mounting of the support profile is possible by means of sideways slideable ducts

- Attachment elements consist of corrosion resistant material

- Overstretch:

- Maximum possible allowed overstretching of the described system, with a wind load qb = 800 Pa:

    - Strip L.050W:  1,900 mm

    - Support profile LD.0440: 1,321 mm

- System depth:

- Strip L.050W and support profile LD.0440: 177 mm

LINIUS® SPECIFICATIONS

Brand	: RENSON LINIUS®

Type 		: L.050W with holder LD.1250 (VV-L-1.3709)

Description:

RENSON LINIUS® lourve system L.050W is compiled from sections of extruded aluminium ALMgSi0.5 that have undergone a surface treatment in accordance with the architect’s specifications. The system consists of water-resistant ventilation strips (tested in accordance with Hevac) – with a large physical free area and an ideal K-factor. It is easily and invisibly mounted due to the assembly clips that fit into the strip holders that form part of the system.

Standards:

- Aluminium alloy: Al Mg Si 0.5 (F25)

- Standardisation: EN AW-6063

- Hardening: T66

- Aluminium pre-treatment:

- Standard DIN 50021 SS

- Strength calculations are based on the following standards:

- ENV 1999-1-1: Calculation of structures in aluminium

- NBN B-03-002-2: Wind load – Dynamic effects

- EN 1991-1-4: Wind load

Surface treatment:

- Natural anodised colour F1 (20 micron): Pre-treated and anodised

- Polyester powder coating in RAL colours (60 to 80 micron): aluminium profiles pre-treated to resist corrosion (DIN 5002155) to guarantee a strong powder layer, and subsequently thermally lacquered

System operation:

- Strips:

- Water-resistant strips with a large clearance, L.050W from extruded aluminium

- Water-resistance classification in accordance with HEVAC (officially tested): A2 through 3 m/s

- Dimensions:

    - Height:  89.6 mm

    - Depth: 130.0 mm

    - Step: 50.0 mm (20 strips across a 1 metre height)

    - Average strip gradient: 44°

- Minimum moments of inertia Iy = 778,472 mm4 (strong axis line); Iz = 100,395 mm4, with a minimum material thickness of 1.8 mm

- Drag coefficient:

    - Cfy (determined by means of wind testing):  1.3 (horizontal direction)

    - Cfz (determined by means of wind tunnel testing):  0.95 (vertical direction)

- Invisibly mounted using clips that fit into the accompanying strip holder L.050W.11 and L.050W.12 (clip joints)

- Physical allowed clearance: 57%

- K-factor: 10.47

- Strip is fitted with 2 screw ducts, suitable for screws of DIN 7982 – ST3.9 mm type

- Inox / stainless steel mesh grid 2.3 x 2.3 mm secured at the back

- Support structure:

- Support profile LD.1250 from extruded aluminium: 36 x 125.0 mm

- Minimum moments of inertia Iy = 1,219,444 mm4

- Strip holders are pre-mounted to the holder profile LD.1250

- Mounting of the support profiles occurs using attachment elements LZ.4211 and LZ.4209 or guiding attachment element LZ.4206

- Attachment elements consist of corrosion resistant material

- Overstretch:

- Maximum possible allowed overstretching of the described system, with a wind load qb = 800 Pa:

    - Strip L.050W:  1,900 mm

    - Support profile LD.1250: 3,038 mm

- System depth:

- Strip L.050W and support profile LD.1250: 258 mm