RENSON WINDOW VENTILATION® SPECIFICATIONS

Brand	: Sonovent®

Type 		: Sonovent® XSmall

Manufacturer and reference:

The Sonovent® XSmall is manufactured and supplied by Renson Ventilation

Tel: 01622 754 123 Email: vents@rensonuk.net

Description:

The RENSON® Sonovent® XSmall is a thermally broken, self-regulating and acoustic window ventilator. The perforated inner profile acts as an insect mesh (removable for cleaning purposes). This window ventilator combines high airflow with high acoustic performances.

Optionally available with Pollux filter: for strongly fine dust and pollen impacted environments.

System operation and performance:

Self-regulating

Thermal conductivity: U-value = 2.8 W/m2K

Watertightness up to 50Pa in open position

Watertightness up to 1200Pa in closed position

Air leakage at 50Pa: <15% in closed position

Airflow and sound reduction:	airslot 10 mm	airslot 15mm	airslot 20 mm	airslot 25 mm

Dn,e,w (C;Ctr) open (dB)			35 (-1;-2) 	32 (-1;-1) 	32 (-1;-1) 	31 (-1;-1)

Dn,e,w (C;Ctr) closed (dB)			n.p.d.		n.p.d.		n.p.d.		n.p.d.

Q at 1 Pa (l/s/m	)			14,5		24,1		25,9		27,5

Q at 1 Pa (m³/h/m)			52,1		86,8		93,3		99,1

Q at 2 Pa (l/s/m	)			20,4		34,1		36,9		39,2

Q at 2 Pa (m³/h/m)			74,5		122,7		132,8		141,4

Q at 10 Pa (l/s/m)			19,1		30,4		29,5		29,9

Q at 20 Pa (l/s/m)			23,6	           	29,4		30,1		28,0

Equivalent area (mm²/m)		18416		30693		32995		35041

Dimensions / Size Range:

Glass reduction (glazed in): 130 mm (flange 20 mm) /135 mm (flange 25 mm)

Height: 105 mm (total height with flange profiles: 145 or 150 mm)

Flange height: 20 or 25 mm

Depth / Total depth: 170 / 205 mm

Fits to glass depths of: 20, 24, 28, 32, 36, 40, 44 mm (other thicknesses available on request)

Maximum length: 2000 mm (glazed-in) or 2500 mm (at transom)

Ventilator Construction:

Profile: manufactured from aluminium alloy Al Mg Si 0.5.

Thermal bridge: extruded uPVC.

Pivoting and self-regulating flap: PVC.

End caps: ASA polymer type Luran S (colour-fast, weather and UV-resistant).

Sound absorbing material: non-combustible mineral wool.

Surface treatment:

Polyester powder coating in any RAL colour (60 to 70 micron): aluminium profiles pre-treated to resist corrosion to guarantee (dual colour possible)

End cap colours: white or black (other colours available on request)

Controls Option:

Manual, rod or cord optional (continuous adjustment).

Motorised: 24V DC (not for glazed-in installations).

Installation:

The Sonovent is suitable for glazed-in installation, installation at transom, installation at compact transom, roof installation, or naked box.

For glazed-in installation and installation at transom, the Sonovent can be supplied in 3 categories:

o    Category 1: With 2 fixed flanges.

Only possible with glass thicknesses of 24 and 28 mm.

Only possible with flange height 25mm.

This version can be used for high-rise projects.

o    Category 2: With 1 fixed outer flange.

There is a fixed flange on the outside and a loose flange on the inside.

Possible with glass thicknesses between 20 and 54mm (increments of 2mm).

Only possible with flange height 25mm.

This version can be used in high-rise projects.

o    Category 3: Special design.

There are loose flanges on the outside and inside.

All even glass thicknesses between 20 and 56mm are possible (increments of 2mm).

This version cannot be used for high-rise projects.

For installation at compact transom, you can choose between a fixed V-size or a V-size of your choice.

A naked box does not contain any flanges.

A fixed V-size of 36 mm is used for roof placement.

Preferably installed at transom (timber, PVC or aluminium). By adding L-profiles to the upper and lower side, the Sonovent® can also be placed on glass. Thermal break positions can change.

Standards:

EN ISO 140-10, EN ISO 717-1, EN 1026, EN 1027, EN 13141-1, EN 12020-2, EN AW 6063 T66, NBN D50-001, EN 1077-2.