RENSON® WINDOW VENTILATION SPECIFICATIONS

Product	: PyrAcoust

Manufacturer and reference:

The PyrAxoust is manufactured and supplied by Renson Ventilation Tel: 01622 754 123

Email: vents@rensonuk.net

Description:

The Renson PyrAcoust is a non-self-regulating acoustic slotvent kit. The external profile has an insect mesh. The Internal slotvent deflects, in open position, the incoming air upwards for an optimal spread of fresh air in the room. The PyrAcoust is available in 2 types: 2500 EA or 5000 EA (other lengths on demand)

Ventilator Construction:

Internal and external profile: manufactured from aluminium alloy Al Mg Si 0.5.

End caps: PP (colour-fast, weather and UV-resistant).

System operation and performance:

Thermal conductivity: U-value: 		n.p.d.

Watertightness: 			n.p.d.

Air leakage (closed): 			n.p.d.

|  | 2500 + 1 Acoustic module | 2500 + 2 Acoustic modules | 5000 + 1 Acoustic module | 5000 + 2 Acoustic modules |
| --- | --- | --- | --- | --- |
| Airflow |  |  |  |  |
| Equivalent area (mm2) | 2748,60 | 2735,88 | 5713,52 | 5596,13 |
| Free area (mm2/m) | 2496 | 2496 | 4472 | 4472 |
| Q at 1 Pa | 2,2 l/s | 2,2 l/s | 4,5 l/s | 4,3 l/s |
| Q at 1 Pa | 7,9 m³/h | 7,9 m³/h | 16,2 m³/h | 15,5 m³/h |
| Q at 2 Pa | 3,2 l/s | 3,1 l/s | 6,4 l/s | 6,2 l/s |
| Q at 10 Pa | 7,6 l/s | 7,5 l/s | 14,4 l/s | 14,5 l/s |
| Q at 20 Pa | 11,1 l/s | 11 l/s | 20,5 l/s | 20,8 l/s |
| Comfort |  |  |  |  |
| Sound reduction Dn,e,w (C;Ctr) |  |  |  |  |
| - in open position | 42 (-1; -2) dB | 45 (-2; -3) dB | 39 (-1; -2) dB | 42 (-2; -4) dB |
| - in closed position | 48 (-1; -3) dB | 50 (-1; -3) dB | 47 (-2; -3) dB | 49 (-2; -4) dB |

Dimensions / Size Range:

|  | 2500 | 5000 |
| --- | --- | --- |
| Height (mm) | 40 | 40 |
| Length (mm) | 250 | 412 |
| Slotsize opening | 192 x 13 | (172 x 13) + 10 + (172 x 13) |

Surface treatment:

Standard: Polyester powder coating in Renson standard white (=AXALTA AE90019148021=BEL 9010), black (RAL9005), grey (RAL7016): aluminium profiles pre-treated to resist corrosion to guarantee.

Other colours on demand.

End cap colours: white, black or grey.

Controls Option:

Continuous adjustment.

Installation:

Installed into window frame (aluminium, timber or uPVC) by fastening endcaps on the ends of the aluminium profiles. It’s advisable to use silicone on the outside hood to guarantee good water seal.

Standards:

EN 13141-1, The Building Regulations-Ventilation-Part F