RENSON LINIUS® L.060M

SPECIFICATION SHEET

LINIUS® L.060M is a ventilation system composed of continuous louvres with the following essential characteristics:

- aesthetically appealing

  - blade pitch: 77 mm

  - blade height: 83 mm

  - invisible assembly with aluminium blade clips

- airflow

  - physical free area: 77%

  - visual free area: 83%

  - aerodynamic properties (without mesh)

    - class 1 according to EN 13030:2001

    - resistance factor entry K = 1/ce² = 4,7  ;  Ce = 0,462

    - resistance factor discharge K = 1/ce² = 4,8  ;  Ce = 0,457

  - documents to be submitted : independent test report in accordance with EN 13030:2001 to determine the aerodynamic properties (BSRIA – 106808/5)

- stability

  - max. unsupported blade span at a peak velocity pressure qp(z) of 800 Pa: 850 mm

  - supporting structure

    - type of mullion and number of mullions are to be provided according to the designed span and the local wind load

    - preferably in aluminium, as part of the continuous louvre system

- materials:

  - extruded aluminium profiles AlMgSi0,5(F25) - T66 - EN AW-6063

  - surface treatment:

    - anodised in natural colour EV6/EV1 (20 micron): pretreated and anodised OR

    - polyester powder coating in RAL colour according to the Qualicoat standard

- options

  - wire mesh 2.3 x 2.3 ; 6 x 6 of 20 x 20 mm, fitted to the rear of the supporting structure

  - threshold profile LZ.4140

  - pre-assembled pivoting ventilation doors with linear blades (see separate description)