**BUILT-IN WALL LOUVRE TYPE RENSON 448/150**

**SPECIFICATION SHEET**

Louvre type Renson 448/150 is a built-in ventilation louvre and has the following properties :

* **Acoustic Performance**

According to :

* + EN ISO 10140:2021
	+ EN ISO 717-1:2020

Tested with dimensions width x height = 1.23m x 1.48m

* + Sound reduction index Rw (C;Ctr) = 11 (-1;-2) dB
	+ Sound reduction related to frequency :

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| F (Hz) | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 |
| R in dB | 7,1 | 4,5 | 4,0 | 6,3 | 12,3 | 13,5 | 12,1 |

* + To be submitted: independent test report (PEUTZ nr. A 4223-2E-RA-001)
* **airflow**
	+ physical free area: 34%
	+ aerodynamic properties according to EN 13030:2001 (with mesh 2.3 x 2.3 mm), tested with dimensions width x height = 1m x 1m.
		- resistance factor entry K = 1/ce² = 16.00 ; ce = 0.250
		- resistance factor discharge K = 1/cd² = 21.24 ; cd = 0.217
	+ To be submitted : independent test report (BSRIA, 104727/2)
* **Weatherability** (EN 13030:2001)
	+ with mesh 2.3 x 2.3 mm (without option water channel)
		- class B at 0.0 m/s air entry or anytime air discharge
		- class C at 0.5 m/s air entry
		- class C at 1.0 m/s air entry
		- class D at 1.5 m/s air entry
	+ documents to be submitted : independent test report (BSRIA, 104727/2)
* **aesthetics**
	+ visual screening
		- horizontally visually closed, by applying a blade pitch which does not exceed the blade height
		- blade pitch = 150mm
		- blade height = 223mm
	+ invisible connections
	+ mitred, pressed corners
* **material**
	+ extruded aluminium profiles (AlMgSi0.5, EN AW 6063 T66)
	+ made with mesh composed of stainless steel 18/8: mesh size 6mm x 6mm
	+ surface treatment:
		- anodised in natural colour EV6/EV1 (20 micron)

**OR**

* + - polyester powder coated
* **fitting depth** : 155mm
* **installation** : according to the instructions of the producer
* **options**
	+ Alternative mesh types: mesh size 2,3mm x 2,3mm or 10mm x 10mm.
	+ Water channel