RENSON LINIUS® L.150ACS

SPECIFICATION SHEET

LINIUS® L.150ACS is a ventilation system composed of continuous louvres with the following essential characteristics:

- Acoustic Performance

According to :

  - EN ISO 140-1:1997 + A1:2004

  - EN 20140-3:1995 + A1:2004

  - EN ISO 717-1:1996 + A1:2006

Tested with dimensions width x height = 1.23m x 1.48m

  - Sound reduction index Rw (C;Ctr) = 11 (-1;-2)

  - Sound reduction related to frequency :

| F (Hz) | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| R in dB | 8,3 | 6,9 | 3,7 | 3,2 | 3,6 | 3,3 | 4,7 | 6,4 | 8,1 | 11,3 | 13,4 | 14,2 | 14,5 | 13,8 | 13,2 | 12,4 |

  - To be submitted: independent test report (IFT-Rosenheim no.164 38195/3e)

- airflow

  - physical free area: 34%

  - visual free area: 54%

  - aerodynamic properties according to EN 13030:2001 (with mesh 2.3 x 2.3 mm), tested with dimensions width x height = 1m x 1m.

    - resistance factor entry K = 1/ce² = 38.58 ;   ce = 0.161

    - resistance factor discharge K = 1/cd² = 35.01 ; cd = 0.169

  - To be submitted : independent test report (BSRIA, 53928/1)

- Weatherability (EN 13030:2001)

  - with mesh 2.3 x 2.3 mm and sill

    - class A at 0.0 m/s air entry or anytime air discharge

    - class B at 0.5 m/s air entry

    - class C at 1.0 m/s air entry

  - documents to be submitted : independent test report (BSRIA, 53928/1)

- aesthetically appealing

  - visual protection

    - horizontally visually closed by applying a blade pitch which does not exceed the blade height

    - blade pitch: 150 mm

    - blade height: 239 mm

  - invisible assembly with aluminium blade clips

- stability

  - impact of wind forces :

    - Cfx :  1,36 (drag - horizontal)

    - Cfy :  1,09 (lift - vertical)

  - max. unsupported blade span at a peak velocity pressure qp(z) of 800 Pa: 2.858 mm

  - supporting structure

    - type of mullion and number of mullions are to be provided according to the designed span and the local wind load

    - preferably in aluminium, as part of the continuous louvre system

- materials:

  - extruded aluminium profiles (AlMgSi0.5, EN AW 6063 T66)

  - surface treatment:

    - anodised in natural colour EV6/EV1 (20 micron): pretreated and anodised

OR

    - polyester powder coating in RAL colour according to the Qualicoat standard

- options

  - wire mesh 2.3 x 2.3 ; 6 x 6 of 20 x 20 mm, fitted to the rear of the supporting structure

  - threshold profile LZ.4140