VARIAVENT®

Renson Ventilation, IZ 2 Vijverdam, Maalbeekstraat 10, 8790 Waregem – België

Tel. +32 (0)56 62 71 11, fax. +32 (0)56 60 28 51, info@renson.be www.renson.eu

DESCRIPTION (text marked in red can be deleted according to your choice)

- Type: thermally broken, self-regulating flap ventilator for glazed-in installation or at transom

- Flexible integrated: in aluminium, timber and PVC window profiles

- Four different airflow levels in same design:

  - high airflow, as much as 28,5 l/s/m at 2Pa

  - integrated airflow limitor in endcap: flow rate can be adjusted manually, without having to dismantle the window ventilation.

  - Visually the same appearance, regardless of flow rate

- iFlux technology:

  - Constant flow rate and reduction of energy losses thanks to the self-regulating valve

  - a self-regulating flap reacts automatically to changes pressure differences / wind strength, and cannot be influenced by the user

  - upward air flow for optimum comfort: coanda-effect

  - air flow adjustable thanks to control lever

- Design inner profile

o Choice between iFlux interior profile with coanda effect and a flat interior profile.

o I-Flux: higher aesthetic comfort due to invisible ventilation openings, higher technical comfort due to airflow that is pushed upwards.

o Flat: visible ventilation openings, ideal in situations with roller blinds.

o Both inner profiles can be removed manually, making them easy to clean.

- Design outer profile

  - Aluminium outer profile ensures clean, straight-lined design

- Waterproof:

  - aluminium external profile acts as a rain cap

  - special foam (compriband) integrated in the end caps to ake the transition between gass and glazed-in vent waterproof

- Insect mesh: perforated interior profile (3 x 3,9 x 11,0 mm)

- Glazed-in installation: glass thickness 20, 24, 28, 32, 36, 40 of 44 mm or at transom (use of additional transom profile)

- Control options: manual, cord or rod

- Finishing

  - aluminium profils: anodised (E6/EV1) / powder-coated in the same RAL colour as the window profiles / bicolor

  - Colour of endcaps = standard mass end caps (best match), mass end caps of your choice, coated endcaps

- Optionaly available with Pollux filter – type 02: for strongly fine dust and pollen impacted environments

- Maximum length: 3000 mm

- Glass reduction: 80 mm

TECHNICAL SPECIFICATIONS

- U value:	 			2,80 W/m²K

- F value:				0,65

- Watertightness up to: 		650 Pa in closed position

- Watertightness up to: 		50 Pa in open position

- Air leakage at 50 Pa:		<15% in closed position

- Sound reduction

  - Dn,e,w (C;Ctr):

- in open position:	25 (-1;-1) dB

- in closed position:	40 (-1;-2) dB

| Properties: |  |
| --- | --- |
| Airflow Q at 1 Pa | 10 l/s/m (S) 15 l/s/m (M) 18 l/s/m (L) 20,9 l/s/m (XL) Manually adjustable with air flow limitor |
| Airflow Q at 1 Pa | 36 m³/h/m (S) 54 m³/h/m (M) 64,8 m³/h/m (L) 75,2 m³/h/m (XL) Manually adjustable with air flow limitor |
| Airflow Q at 2 Pa | 14,2 l/s/m (S) 21,4 l/s/m (M) 25,6 l/s/m (L) 28,5 l/s/m (XL) Manually adjustable with air flow limitor |
| Airflow Q at 2 Pa | 51,3 m³/h/m (S) 76,9 m³/h/m (M) 92,3 m³/h/m (L) 102,6 m³/h/m (XL) Manually adjustable with air flow limitor |
| Airflow Q at 10 Pa | 12,7 l/s/m (S) 19,1 l/s/m (M) 22,9 l/s/m (L) 25,4 l/s/m (XL) Manually adjustable with air flow limitor |
| Equivalent area | 12725 / 19088 / 22905 / 26595 mm²/m |
| Airflow Q at 20 Pa | 13,6 l/s/m (S) 20,4 l/s/m (M) 24,4 l/s/m (L) 27,1 l/s/m (XL) Manually adjustable with air flow limitor |
| Self-regulating | Yes |
| Surface area | 0,097 m²/m |