BUILT-IN WALL LOUVRE TYPE RENSON 421RC3

SPECIFICATION SHEET

Louvre type Renson 421RC3 is a built-in ventilation louvre and has the following properties :

- aesthetics

  - visual screening

    - horizontally visually closed, by applying a blade pitch which does not exceed the blade height

    - blade pitch = 50 mm

    - blade height = 56 mm

  - invisibly assembled with aluminium blade supports

  - invisible mounting of the louvre with stainless steel wall anchors

  - mitred, pressed corners

  - flange = 38mm

- burglar resistance (according to EN1627 up to and including EN1630 (2011))

  - Classification: RC3 (for louvre surfaces up to 4.8 m²)

  - documents to be submitted : independent test report (WTCB-BBRI)

- airflow

  - physical free area: 43%

  - visual free area: 70%

  - aerodynamic properties according to EN 13030:2001 (with mesh 2.3 x 2.3 mm)

    - resistance factor entry K = 1/ce² = 13.82  /  Ce = 0.269

    - resistance factor discharge K = 1/cd² = 12.85  /  Cd = 0.279

  - documents to be submitted : independent test report in accordance with EN 13030:2001 to determine the aerodynamic properties (BSRIA, 54763/2)

- Weatherability

  - Overlapping Z-shaped blades with water barrier

- material

  - extruded aluminium profiles (AlMgSi0.5, EN AW 6063 T66)

  - made with mesh composed of stainless steel 18/8: mesh size 2.3 x 2.3 mm

  - surface treatment:

    - anodised in natural colour EV6/EV1 (20 micron): pretreated and anodised OR

    - polyester powder coating in RAL colour according to the Qualicoat standard

- fitting depth : 46 mm

- options

  - Alternative mesh types: mesh size 6mm x 6mm or 10mm x 10mm.

  - Water channel for increased weatherability

  - Drainage profile to prevent dirt deposits on the facade

  - Removable mesh: allows easy cleaning and comes with an integrated drainage profile

  - Filter: class G4