

3/3

specification sheet

452

LOUVRE

manufacturer

RENSON Ventilation, IZ 2 Vijverdam, Maalbeekstraat 10, 8790 Waregem – Belgium

tel. +32 (0)56 62 71 11, fax. +32 (0)56 60 28 51, info@renson.be  www.renson.eu

series

BUILT-IN

Wall louvre 

WITH chevron section BLADES 

types

452

description

The 452 louvre is a built-in wall louvre with large chevron section V-blades and excellent watertightness (class A, up to 1.0 m/s according to EN13030).

Extruded, L-shape, aluminium frame profiles with a total height of 64 mm are cut at mitre of 45° and assembled through compression and a clamping corner.

Aluminium blade supports are pop-riveted to the perforated vertical frame profiles.

Louvres with a width over 700 mm are provided with an extra perforated U-profile to fit supplementary blade supports for reinforcement.

The extruded aluminium blades are clipped into the blade supports. The distance between the blades is 66 mm. The blades are V-shaped, allowing no see-through visibility. 

An anti-static 304 stainless steel 6 x 6 mm mesh wire is tensioned tight inside the frame using a nylon wire.

The finish can be anodised (natural) or powder-coated (any RAL colour). 
Minimum dimensions are 305 x 305 mm (WxH) 

For larger sizes, multiple 452 louvres may be linked together on request.

The louvre is optionally available with a frame without flange.

A version for installation in window frames is also available on request.

material & finish

Blades and frame profile: aluminium AlMgSi 0.5 (according to EN 12020-2 and EN AW-6063)

Finish: natural (SAA) anodised (20 micron) or powder-coated (60-70 micron) in any RAL colour 

Mesh: standard anti-static 304 stainless steel 6 x 6 mm mesh wire, tensioned tight inside the frame using a nylon wire.

Note: louvres with a width over 700 mm are provided with an extra perforated strengthening U-profile to fit supplementary blade supports for reinforcement.

dimensions

Depth to fit

: 81.5 mm
Blade pitch

: 66 mm

Flange size

: 50 mm

Total thickness

: 86.5 mm

Minimum dimensions
: 305 mm x 305 mm (W x H)

Maximum dimensions
: on request (W X H)

INSTALLATION

Should be installed in accordance with installation instructions, using plugs and screws as appropriate for the wall and/or surface material (not included in the delivery).

Wall brackets nr. 429 for securing against the wall are included in the delivery.
Note: A reinforcing backstructure is required for louvres of more than 3m2.
optional extras

· Water channel: installed under the lowest blade; provides enhanced water drainage. This water channel is made of aluminium AlMgSi 0.5, anodized and powder-coated in the same finish as the louvre.

· Insect mesh: anti-static, 304 stainless steel 2.3 x 2.3 mm insect mesh or 10 x 10 mm bird mesh.

· Removable insect mesh: anti-static, 304 stainless steel 2.3 x 2.3 mm insect mesh / 6 x 6 mm wire mesh / 10 x 10 mm bird mesh with integrated water channel.

Technical specifications

452

Airflow:  

· K-factor, supply:

66,1
· K-factor, extraction:

79,7
· Ce coefficient:

0,123
· Cd coefficient:

0,112
Free area:

· Visual free area
70%

· Physical fee area
41%

Protection:

· IP class: 


2XD

· HEVAC-class 0.0m/s: 
A 
· HEVAC-class 0.5m/s: 
A 
· HEVAC-class 1.0m/s: 
A 
· HEVAC-class 1.5m/s: 
B 
· HEVAC-class 2.0m/s: 
D
· Resistance class: 

n.p.d.
Sound reduction Rw (C;Ctr): 

· Open:


n/a 

standards

This product is manufactured according to, complies with and/or has been tested according to:

EN ISO 140-10

EN ISO 717-1

EN 12020-2

EN AW 6063 T66

EN 13030

EN 60529

RENSON reserves the right to make technical changes.

TPD-452-09BT-001-20100301-EN

