BUILT-IN WALL LOUVRE TYPE RENSON 448/225

SPECIFICATION SHEET

Louvre type Renson 448/225 is a built-in ventilation louvre and has the following properties :

- Acoustic Performance

According to :

  - EN ISO 10140:2021

  - EN ISO 717-1:2020

Tested with dimensions width x height = 1.23m x 1.48m

  - Sound reduction index Rw (C;Ctr) = 14 (-0;-3) dB

  - Sound reduction related to frequency :

| F (Hz) | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| R in dB | 9,6 | 5,3 | 4,7 | 8,4 | 16,6 | 21,5 | 16,7 |

  - To be submitted: independent test report (PEUTZ nr. A 4328-3E-RA-001)

- airflow

  - physical free area: 34%

  - aerodynamic properties according to EN 13030:2001 (with mesh 2.3 x 2.3 mm), tested with dimensions width x height = 1m x 1m.

    - resistance factor entry K = 1/ce² = 20.29 ;   ce = 0.222

    - resistance factor discharge K = 1/cd² = 23.11 ; cd = 0.208

  - To be submitted : independent test report (BSRIA, 105079/4)

- Weatherability (EN 13030:2001)

  - with mesh 2.3 x 2.3 mm (without option water channel)

    - class C at 0.0 m/s air entry or anytime air discharge

    - class C at 0.5 m/s air entry

    - class D at 1.0 m/s air entry

  - documents to be submitted : independent test report (BSRIA, 105079/4)

- aesthetics

  - visual screening

    - horizontally visually closed, by applying a blade pitch which does not exceed the blade height

    - blade pitch = 150mm

    - blade height = 312mm

  - invisible connections

  - mitred, pressed corners

- material

  - extruded aluminium profiles (AlMgSi0.5, EN AW 6063 T66)

  - made with mesh composed of stainless steel 18/8: mesh size 6mm x 6mm

  - surface treatment:

    - anodised in natural colour EV6/EV1 (20 micron)

OR

    - polyester powder coated

- fitting depth : 230mm

- installation : according to the instructions of the producer

- options

  - Alternative mesh types: mesh size 2,3mm x 2,3mm or 10mm x 10mm.

  - Water channel