**SURFACE MOUNTED LOUVRE TYPE RENSON 431RC2 RAV**

**For Reynaers Aluminium motorized ventilation vent**

**SPECIFICATION SHEET**

Louvre type Renson 431RC2 RAV is a surface mounted ventilation louvre and has the following properties :

* **burglar resistance** (according to EN1627 (May 2011) and EN1628:2011+A1 up to and including EN1630:2011+A1 (2011) )
	+ Classification: RC2
	+ documents to be submitted : independent test report (WTCB-BBRI)
* **fall-through safety**
	+ according to EN13049(2003)
		- class 5
		- documents to be submitted : independent test report (WTCB-BBRI / Wintech by UL)
	+ according to BS 6180:2011
		- passed for UDLL 0.74 kN/m, point load 0.5 kN and UDL 1.0 kN/m²
		- documents to be submitted : independent test report (WTCB-BBRI / Wintech by UL)
* **airflow**
	+ physical free area: 41%
	+ visual free area: 59%
	+ aerodynamic properties according to EN 13030:2001 (with mesh 2.3 x 2.3 mm)
		- resistance factor entry K = 1/ce² = 23.56 / Ce = 0.206
		- resistance factor discharge K = 1/cd² = 25.51 / Cd = 0.198
	+ documents to be submitted : independent test report in accordance with EN 13030:2001 to determine the aerodynamic properties (BSRIA, 54763/7)
* **weatherability**
	+ Overlapping Z-shaped blades
* **aesthetics**
	+ visual screening
		- horizontally visually closed
		- blade pitch = 33.33 mm
	+ mitred, pressed corners
* **material**
	+ extruded aluminium profiles (AlMgSi0.5, EN AW 6063 T66)
	+ made with mesh 2.3 x 2.3 mm INOX 304
	+ surface treatment:
		- anodised in natural colour EV6/EV1 (20 micron): pretreated and anodised **OR**
		- polyester powder coating in RAL colour according to the Qualicoat standard
* **louvre depth** : 32mm
* **installation**
	+ according to the instructions of the producer
	+ with burglar proof screws type Secufast Pin Hexagon Ø 4,2 x 38 mm
* **options**
	+ Alternative mesh types: 2,3 x 2,3 mm INOX 316