SURFACE MOUNTED LOUVRE TYPE RENSON 431RC2 RAV

For Reynaers Aluminium motorized ventilation vent

SPECIFICATION SHEET

Louvre type Renson 431RC2 RAV is a surface mounted ventilation louvre and has the following properties :

- burglar resistance (according to EN1627 (May 2011) and EN1628:2011+A1 up to and including EN1630:2011+A1 (2011) )

  - Classification: RC2

  - documents to be submitted : independent test report (WTCB-BBRI)

- fall-through safety

  - according to EN13049(2003)

    - class 5

    - documents to be submitted : independent test report (WTCB-BBRI / Wintech by UL)

  - according to BS 6180:2011

    - passed for UDLL 0.74 kN/m, point load 0.5 kN and UDL 1.0 kN/m²

    - documents to be submitted : independent test report (WTCB-BBRI / Wintech by UL)

- airflow

  - physical free area: 41%

  - visual free area: 59%

  - aerodynamic properties according to EN 13030:2001 (with mesh 2.3 x 2.3 mm)

    - resistance factor entry K = 1/ce² = 23.56  /  Ce = 0.206

    - resistance factor discharge K = 1/cd² = 25.51  /  Cd = 0.198

  - documents to be submitted : independent test report in accordance with EN 13030:2001 to determine the aerodynamic properties (BSRIA, 54763/7)

- weatherability

  - Overlapping Z-shaped blades

- aesthetics

  - visual screening

    - horizontally visually closed

    - blade pitch = 33.33 mm

  - mitred, pressed corners

- material

  - extruded aluminium profiles (AlMgSi0.5, EN AW 6063 T66)

  - made with mesh 2.3 x 2.3 mm INOX 304

  - surface treatment:

    - anodised in natural colour EV6/EV1 (20 micron): pretreated and anodised OR

    - polyester powder coating in RAL colour according to the Qualicoat standard

- louvre depth : 32mm

- installation

  - according to the instructions of the producer

  - with burglar proof screws type Secufast Pin Hexagon Ø 4,2 x 38 mm

- options

  - Alternative mesh types: 2,3 x 2,3 mm INOX 316