SPECIFICATION SHEET (Belgium): AEROO

Version 07/03/2024

AEROO is an adjustable design valve for both pulsion and extraction. AEROO’s aerodynamically refined design makes it the quietest on the market.

MATERIAL

Material: ASA UPVC

Dimensions:

- Valve connection: Ø125 mm

- Front plate: round Ø170 mm/square 170 x 170 mm

Colour:  RAL 9010 (coating can be applied on top)/9005

Mounting: self-clamping rubber

SPECIFICATIONS

∫One valve for both pulsion (up to 90 m³/hr) and extraction (up to 100 m³/hr)

Maximum airflow

- Pulsion side up to 90 m3/h at 21 dB(A)

  - bedroom: up to 75 m3/h at <10 dB(A)

- Extraction side from 100 m3/h at 26.5 dB(A)

Acoustic aspects = Extremely quiet:

- At 90 m³/h pulsion 21 dB (A) in open position without air blocker

- At 100 m³/h extraction 26.5 dB (A) in open position without air blocker

Lowest resistance (in open position) = reduction of central unit energy consumption and noise production

- Pressure drop of 8 Pa in open position and without air blocker at 90 m³/h flow

- Pressure drop of 14 Pa in open position and without air blocker at 100 m³/h flow

Air flow:

- Perfect Coanda pulsion technology ensures comfort and avoids draughts

Endlimit settings:

- Valve with 50 finely tunable endlimit settings while still maintaining whisper-quiet operation throughout a wide operating range

- 2 regulation methods

  - Manual dial with pre-printed letters for better visibility

  - Adjusted key opening for use of setting tool from ground floor

= no ladder necessary

Regulation optimisation (optional)

- Automatic calculation of regulation position per valve possible via algorithm (in combination with high-performance demand-driven D+ ventilation units)

Installation:

- Double function sealing ring

  - Fixing the valve & sealing it airtight

  - no tools or mounting materials required for installation

- Valve assembled and in ‘open position’ in packaging = time saving & installation-ready

- Immediately ready for initial measurement after installation

  - Front plate loose in packaging = time savings & no damage during installation

Cleaning and maintenance:

- Easily removable front plate, without having to remove the connection

  - Valve retains settings during cleaning

  - No damage to ceiling upon removal

REFERENCES

| Valves | White (RAL 9010) | Black (RAL 9005) |
| --- | --- | --- |
| Aeroo Round | 17147 | 17831 |
| Aero Square | 17148 | 17832 |
| Aeroo Round bulk packaging | 30880 | - |

| Accessories |  |
| --- | --- |
| Aeroo Air blocker | 12158 |
| Aeroo set-up help | 17149 |