GLAZED-IN LOUVRE TYPE RENSON 494

SPECIFICATION SHEET

Louvre type Renson 494 is a glazed-in ventilation louvre and has the following properties:

Airflow

- physical free area: 26%

- aerodynamic properties according to EN 13030:2001 (with mesh 6 x 6 mm)

  - resistance factor entry K = 123,5  ;  ce = 0,090

  - class 4

- documents to be submitted: independent test report (BSRIA, 53355/1)

Weatherability

- with mesh 6 x 6 mm and water channel

  - according EN 13030:2001

    - class A at 0.5 m/s air entry

    - class C at 1.0 m/s air entry

    - to be submitted: independent test report (BSRIA, 53355/1 - 104727/1)

aesthetics

- visual screening: horizontally visually closed

- blade pitch = 33.33 mm

- visual free area: 56%

- invisibly assembled with aluminium blade supports

- mitred corners

material

- extruded aluminium profiles (AlMgSi0.5, EN AW 6063 T66)

- made with mesh composed of stainless steel 18/8: mesh size 6 x 6mm

- surface treatment

  - anodised in natural colour EV6/EV1 (20 micron): pretreated and anodised

OR

  - polyester powder coating in RAL colour according to the Qualicoat standard

Dimensions

- frame thickness: 24mm / 28mm / 32mm OR other

- width x height / diameter / ... : see bill of quantities and/or drawings

options

- alternative mesh types: mesh size 2.3mm x 2.3mm or 10mm x 10mm.

- water channel for increased weatherability: class A at 0,5 m/s

- drainage profile to prevent dirt deposits on the façade

- removable mesh: allows easy cleaning and comes with an integrated drainage profile

- filter: class G4

- 414THF: Themally broken

- 414VA: ininitely variable

- welded blades