RENSON WINDOW VENTILATION® SPECIFICATIONS

Brand	: Sonovent®

Type 		: Sonovent® Compact 10 / 13 / 15 mm air slot

Manufacturer and reference:

The Invisivent® EVO HF is manufactured and supplied by Renson Ventilation Tel: 01622 754 123 Email: vents@rensonuk.net

Description:

The RENSON® Sonovent® Compact is a self-regulating, thermally broken, acoustic  window ventilator. Perforated inner profile (3 x 17mm) acts as an insect mesh and is removable.

System operation and performance:

Self-regulating: P3 (good self-regulating).

Air leakage: 50Pa < 15%

Thermal conductivity: U-value = 3.45 W/m2K.

Watertightness: closed position 650Pa and open position 150Pa.

Airslot  10	Airslot 13	Airslot 15

Dn,e,w (C;Ctr) open (dB)		36 (0;-1) 	35 (0;-1)	33 (0;-1)

Dn,e,w (C;Ctr) closed (dB)		n.p.d		n.p.d		n.p.d

Q at 1 Pa m³/hr/m		43,3		54,5		68,8

Q at 2 Pa m³/hr/m		58,9		67,7		71,5

Q at 1 Pa l/s/m			12,1		15,2		19,4

Q at 2 Pa l/s/m			16,4		18,8		19,9

Equivalent area: mm²/m	15334		19278		24687

Dimensions / Size Range:

Glass reduction: 78mm.

Height: 95mm.

Depth (bottom): 145 mm.

Fits to glass depths of: 20, 24, 28, 32 and 36 mm (other thicknesses available on request).

Maximum length: 2000mm (glass) 2500mm (transom).

Ventilator Construction:

Profile: manufactured from aluminium alloy Al Mg Si 0.5.

Thermal bridge: PVC.

Pivoting and self-regulating flap: PVC.

End caps: ASA polymer type Luran S (colour-fast, weather and UV-resistant).

Sound absorbing material: non-combustible mineral wool.

Surface treatment:

Satin anodised (EV6/EV1-SAA) (20 micron): pre-treated and anodised.

Polyester powder coating in any RAL colour (60 to 70 micron): aluminium profiles pre-treated to resist corrosion to guarantee (dual colour possible).

End cap colours: white or black (other colours available on request).

Controls Option:

Manual: Cord and rod optional (continuous adjustment).

Motorised: 24V DC (continuous adjustment).

Installation:

Intended to be glazed-in or at transom (timber, PVC or aluminium) with the additional transom profile.

Standards:

EN ISO 140-10, EN ISO 717-1, EN 1026, EN 1027, EN 13141-1, EN 12020-2, EN AW 6063 T66, NBN D50-001, EN 1077-2.