BUILT-IN WALL LOUVRE TYPE RENSON 480

SPECIFICATION SHEET

Louvre type Renson 480 is a built-in ventilation louvre and has the following properties :

- aesthetics

  - visual screening

    - horizontally visually closed, by applying a blade pitch which does not exceed the blade height

    - blade pitch = 60 mm

    - blade height = 60 mm

  - invisibly assembled with aluminium blade supports

  - Invisible mounting of the louvre with wall anchors no. 429.

  - mitred, pressed corners

  - flange = 50 mm

- airflow

  - physical free area: 76%

  - visual free area: 90%

  - aerodynamic properties (with mesh 6 x 6 mm)

    - class 1 according to EN 13030:2001

    - resistance factor entry K = 1/ce² = 5,03 ;  Ce = 0,446,

    - resistance factor discharge K = 1/cd² = 4,96  ;  Cd = 0,449

  - documents to be submitted : Official test report (BSRIA – 54763/3) in accordance with EN 13030:2001 to determine the aerodynamic properties

- weatherability

  - Z-shaped blades with water barrier

- stability

For louvres larger than 3 m², a reinforcing mullion to be provided.

- material

  - extruded aluminium profiles (aluminium AlMgSi0.5, EN AW 6063 T66)

  - made with mesh composed of stainless steel 18/8: mesh size 6 x 6 mm

  - surface treatment:

    - anodised in natural colour EV6/EV1 (20 micron): pretreated and anodised OR

    - polyester powder coating in RAL colour according to the Qualicoat standard

- fitting depth : 82 mm

- options

  - Alternative mesh types: mesh size 2,3mm x 2,3mm or 10mm x 10mm.

  - Water channel and mesh 2,3 x 2,3 mm for increased weatherability

  - Drainage profile to prevent dirt deposits on the facade

  - Removable mesh: allows easy cleaning and comes with an integrated drainage profile

  - Filter: class G4

  - Without flange