RENSON LOUVRE SPECIFICATIONS 
Brand

: LOUVRE PANEL
Type 

: 424RC2 – BURGLAR PROOF GLAZED-IN 50mm pitch wall louvre
Manufacture and reference :

The 424RC2 Louvre Panel is manufactured and supplied by Renson Fabrication Ltd.  Tel: 01622 754123 
Email: louvres@rensonuk.net Website: www.renson.eu

Description:
RENSON 424RC2 is a high duty extruded aluminium burglar proof louvre panel using a L.050 pitch blade mounted into an integrated frame. It is designed to be glazed into a pre formed opening. 
System operation and performance:  

Type



424RC2
Visual Free Area

70%

Physical Free Area

43%

K-factor: Intake


13.82

K-factor: Discharge

12.85

Ce coefficient: Intake

0.269
Cd coefficient: Discharge
0.279
Watertightness (HEVAC) – Class B (with water channel) at 0.5m/s
Burglarproof
Louvre 424RC2 is burglarproof according to class RC2, certificate surface 0,641 < o < 4,68 m², in accordance with EN1627 up to and including EN1630 (September 2011).
Dimensions/Size Range:

Minimum Dimensions (mm)
220 x 200

Thickness (mm)

24 or 28
Pitch (mm)


50
Product Construction:
Profile: Extruded aluminium (EN 12020-2)

Surface Treatment:

Mill finish

Anodised (EV6/EV1) (20 micron): pre-treated and anodised.

Polyester powder coating in any RAL colour (40 micron): aluminium profiles pre-treated to resist corrosion to guarantee.

Installation:

To be fitted like double glazing
Accessories

Stainless steel birdguard 6mm x 6mm secured to the rear

Stainless steel insect mesh 2.3mm x 2.3mm secured to the rear

Water channel
Product Information:
http://www.rensonuk.net/Louvres-panels-United-Kingdom.html
